## Slide 1
Towards Automatic Context Inference
for Sensors in Commercial Buildings

## Slide 2
Notes: People spend 93% of time indoors and providing a comfortable env can improve 8-11% productivity.
To ensure\\ that these buildings operate normally and are comfortable throughout diff weather conditions,
we need to assess and control various factors\\, such as air circulation, heat flow, moist. lv, or lgt cond.
To this end, 1000s of sensors are installed to monitor the pressure in every duct, status of every water pipe, and the kw consumption on every circuit.

## Slide 3
Comfort
Correctness
Maintenance
Zone Temp 2 RMI204
Temp Floor 1 Area1
SODA1R300__ART
SODA1R410B_ART
Notes: On top of these sensors, nuanced intelligent analytics are running continuously\\
in order to optimize the comfort\\ assure the correctness\\ identify faulty and dysfunctional equip.
As an example, an analytics that detects overheated rooms would need to locate and pull data from the tmp & tmp stpt in each room.
Contextual information about the type and location of sensors is usually extracted from the so-called point names, e.g., right bttm in bldg1: see certain structure and volcab\\ another two look completely diff\\
in other words, diff buildings use diff vocabularies and conventions for the pt names

## Slide 4
Zone Temp 2 RMI204
Temp Floor 1 Area1
SODA1R300__ART
SODA1R410B_ART
Comfort
Correctness
Maintenance
Comfort
Correctness
Maintenance
Metadata Mapping
Notes: Consequently, as a first step in running analytics, we need to create\\ a match btw the data streams and the inputs of AE\\
This process is called metadata mapping and is currently a manual process performed on a per building basis

## Slide 5
SODA1R300__ART
Bldg: xxx
Zone: xxx
Room: xxx
Type: xxx
SOD
1
300
Room Temperature
Notes: As an example, here is the pn for a tmp|| to extract the info\\ a technician with domain knowledge\\ needs to manually segment the pt names and decode\\ the information, e.g.
It takes weeks for a typical bldg with thousands of sensors&pts|| not scalable to the Ms of bldgs
besides, mapping one bldg could be 1M business\\, and this cost eats into the potential savings.

## Slide 6
lux
AHU
VAV
AHU: Air Handling Unit
VAV: Variable Air Volume
?
?
?
?
?
Notes: We want to predict types\\, based on that we also need to know the relations between points\\
e.g., there are a handful of ahus, where each h/c air and cirs to dozens of vavs, and the vav further fine tunes the air to a space. one type of important relation is the functional connection btw ahu & vav\\, which we want to idtfy by fan&flow - issue in a vav, track down ahu\\,
or co-located sensors to assess if a room is comfortable.\\

## Slide 7: Sensor context can be inferred using names and data with minimal manual effort compared to existing solutions
Hypothesis
Notes: baseline?

## Slide 8
Automatic type inference
  Leverage existing building(s) while no two buildings are identical
Automatic relation inference
  Huge search space for possible pairwise relations
Technical Challenges

## Slide 9
Automatic type inference
Automatic relation inference
  Functional connection between equipment
  Co-location
Toolkit for mapping to a uniform format (Brick schema)
Thesis Contributions

## Slide 10
Automatic type inference
Automatic relation inference
  Functional connection between equipment
  Co-location
Toolkit for mapping to a uniform format (Brick schema)

## Slide 11
SODA1R300_ART
SODA2R214_ART
SODA-ZONE2ART
SODA-AHU9-SFS
SODA3AHU7-SFS
1
Zone1 Temp RMI328
Space RMI530 TMP
DA Humiditydac4UIP17
Notes: In a bldg., given names and data of sensors which are shown as a row, the goal is to automatically predict the type.
we usually have well mapped bldgs\\ and we want to leverage them; however, a challenge is how to transfer the info
On the one hand, pt name\\ is a good indicator of the type, but the pattern/convention does not generalize across buildings;
On the other hand, TS data\\ is more likely to be similar between buildings, e.g., rmt is 70-78 no matter in which building
so we transfer the info in mapped buildings by training a clf using data features+type labels\\ and apply the clf to the df in the new bldg to predict types

## Slide 12
SODA1R300_ART
SODA2R214_ART
SODA-ZONE2ART
SODA-AHU9-SFS
SODA3AHU7-SFS
2
1
Notes: we can train a different clf that learns a different perspective from the data features, and gives preds

## Slide 13
SODA1R300_ART
SODA2R214_ART
SODA-ZONE2ART
SODA-AHU9-SFS
SODA3AHU7-SFS
3
1
2
Notes: and similarly a third

## Slide 14
SODA1R300_ART
SODA2R214_ART
SODA-ZONE2ART
SODA-AHU9-SFS
SODA3AHU7-SFS
1
2
3
0.67
0.33
0.67
Notes: however, each clf can give a different prediction\\, e.g., || how to effectively adopt the preds?\\
people tend to name the same type of sensors similarly||, e.g., top3 & bottom2, so we look at how much each clf's preds agree with the name clusters, in order to quantify its confidence
e.g., we cluster names\\ and get 2 groups, we see that out of the 3 sensors\\, 2 are predicted as temps by clf1-- so we get 2/3 agreement and we assign 0.67\\ we do so\\ for each clf and take a weighted sum, e.g., 1st predicted as rmt\\
note, in some cases, the agreement can be too low, and we discard the predictions

## Slide 15: Evaluation Dataset
A: Rice Hall
B: Soda Hall
C: Sutardja Dai Hall
3 buildings on 2 campuses
2,500+ sensing and control points
22 types

## Slide 16: Type Classification Accuracy by Transfer Learning
Cov: % labeled
Acc: % of labels are correct
Notes: x-axis: threshold
metrics, two-way transfer
the way to look at this fig: 96acc/72cov 85acc/92cov
trend: in both cases, as acc goes up, cov goes down

## Slide 17: Related Work
-Still require manual effort
-Work within a building
Schumann et al. - BuildSys’14
Bhattacharya et al. - BuildSys’15
Balaji et al. - BuildSys’15
Gao et al. - BuildSys’15
Koh et al. - BuildSys’18

## Slide 18
Automatic type inference
Automatic relation inference
  Functional connection between equipment
  Co-location
Toolkit for mapping to a uniform format (Brick schema)

## Slide 19
lux
AHU
VAV
Notes: all this info now manual and auto is challenging: search space is huge considering possible #pairwise relations
Key: as they are connected, exposed to same events (fan, person), we would observe correlated events

## Slide 20
AHU
VAV
Notes: As an example, the fan speed of an AHU in blk, and the airflow in a connected VAV in red.
We see when fan changes\\, we also observe corresponding changes in vav
How do we detect the events?

## Slide 21
Outlier Detection?
Notes: OD will get the big one\\, many others look like no-event\\
if we tune the parameter to get 2nd, we will obtain many FPs.

## Slide 22
Edge Detection?

## Slide 23
Kinematics?
Steady
Gradual
Drastic
Notes: We consider the kinematic state of data: steady vs dynamic
\\e.g., the orange is steady\\blue gradual\\green drastic
%We model the state in data and consider the changes in state as events
The basic idea is to estimate the state of each reading || and the state determines how the data progresses over time, in terms of velocity and noise lv.\\

## Slide 24: Switching Kinematic Model
latent true values
observed values
e.g., airflow readings
xt-1
xt
xt+1
yt-1
yt
yt+1
zt-1
zt
zt+1
latent states
e.g., event or steady
Markovian state sequence
True value mapping
Kinematics transitions
Notes: More formally, the model is the following: vars \\top layer decides the state\\ and affects how data progress (vel, nosie) which is expressed by the 2nd layer\\ we also model the true values
what’s new here: globally learn the para\\consider both backwards and forwards info

## Slide 25: Example Output
VAV
AHU 1
AHU 2
Notes: Example output of the event model: a vav and its connected AHU, and a non-connecting AHU.
We see the top correlates better with the 2nd than the 3rd; the intuition however is to use only events caused due to the connection\\e.g., green
Besides these correlated events, VAVs are also affected by the activities in served space.

## Slide 26: Sift Out Coincident Events
Correlation Before After
<top, mid>: 0.73 0.87
<top, bottom>: 0.59 0.21
AHU
VAV 1
VAV 2
Notes: Masking to the rescue: when correlating a vav to an ahu, we only use events in the vav at T where ahu has events\\ e.g., (the pink ones)\\ essentially what this is doing is: when there is e in ahu, we want to see if there are also e in vav, coz we believe connected a-v will have coin'ed Es.
more quantitatively, masking increases the corr between connected equip
the assignment is argmax

## Slide 27: Evaluation Dataset
 | A | B | C | D | E
# of VAV | 261 | 113 | 195 | 510 | 259
# of AHU | 12 | 8 | 5 | 13 | 8
# of Sensor | 2,754 | 1,318 | 2,010 | 4,811 | 2,379
Possible Search Space: 8113 ~= 10102
Notes: #vav per ahu vary from 5 - 20+

## Slide 28: Functional Relation Accuracy
Chart: 
| Random | Correlation | Canny Edge | Kalman Filter | Switching Kinematic Model
Method | 10.8 | 58.41 | 69.91 | 80.59 | 92.38
Inference Accuracy (%)
Notes: Explain baselines\\

## Slide 29: Effect of Amount of Data
Notes: As we look for more correlated events over a longer time, the chance of correlation by chance drops.

## Slide 30
lux
AHU
VAV
Notes: The principle of looking for correlated events also applies to co-location

## Slide 31
RM 1
RM 3
RM 2
Objective:
Higher sum of all red edges
lux
lux
lux
3.5
4.2
3.1
4.8
2.8
…
Notes: We want to assign sensors into rooms, and assume one for each type. color of the sensor indicates ground truth room membership.
we randomly assign them as a starting piont.\\ coz we believe co-located exposed to same Es, the optimal assignments should have the largest intra-room corr, indicated by the red edges
So we optimize\\ for a higher sum of the red edges, and when the sum is highest, we reach a solution.
Genetic algorithm: generate candidates by swapping pairs of same type\\, e.g., \\ \\
we rank these candidates and replace the ones low on the rank with the top ones – as in natural selection – the best survive

## Slide 32
RM 1
RM 3
RM 2
Objective:
Higher sum of all red edges
lux
lux
lux
4.2
4.8
…
4.2
4.8
3.5

## Slide 33: Evaluation Dataset
200 streams from 50 rooms in one office building
4 types: CO2, humidity, light, temperature
One week’s data
Possible Search Space: (50!)4 ~= 8.5 * 10257

## Slide 34: Co-location Accuracy
Event
Raw
EMD
lux
Notes: explain baselines and axis
looking for correlated events is effective in identifying co-located sensors

## Slide 35: Co-location Accuracy
Notes: Each col, each row, and order of rows (by co2)
Errors only occur in nearby rooms
Different accuracy metric ~90%

## Slide 36: Related Work
Smith et al. - SigBED’12
Koc et al. - BuildSys’14
Bharttacharya et al. - BuildSys’15
Koh et al. - Arxiv’16
-Different Relations
-Require Perturbation

## Slide 37
Automatic type inference
Automatic relation inference
  Functional connection between equipment
  Co-location
Toolkit for mapping to a uniform format (Brick schema)

## Slide 38
Power Meter
Supply Fan
VAV
Damper
Return Fan
AHU
VAV
AHU
Damper
feeds
Power Meter
hasPoint
hasPart
HVAC Zone
feeds
Brick has been integrated into the ASHRAE Standard 223P for semantic tagging of building data
Notes: After extracting the contextual information, we need to express it in a uniform format, i.e., a schema
Brick has an expressive and comprehensive vocabulary to represent the entities and their relationships\\ triplet predicate: e.g. \\ \\
it enables efficient and convenient queries.

## Slide 39
Automatic type inference
Automatic relation inference
  Functional connection between equipment
  Co-location
Toolkit for mapping to a uniform format (Brick schema)

## Slide 40: Plaster Architecture
De-noising
Data Feature Extractor
Smoothing
Scrabble1
Zodiac2
Building Adapter
Prog. Synthesis3
Output Brickifier
Evaluator
Visualizer
Data Preparation
Algorithm
Utility
Feature Engineering
Model Training
Delivery
Input Brickifier
Text Feature Extractor
Canonical ML
1[KBSMAG BuildSys’17] 2[BVNA BuildSys’15] 3[BHCOWW BuildSys’15]
Notes: Plaster consists of reusable modules, and provides unified interfaces to construct algorithms and enable them to connect with each other.
e.g., BA learns type faster than zodiac

## Slide 41: Workflows
from plaster.utils import DataLoader
from plaster.utils import Dataset
from plaster.utils.preprocessing import denoise, smooth
from plaster.algorithms import BuildingAdapter
from plaster.algorithms import Scrabble
from plaster.workflow import Workflow
raw_data = DataLoader(building=‘rice’)
dataset = Dataset(raw_data, type=‘time_series’, preprocessing=[denoise,smooth])
model1 = BuildingAdapter(batch_size=1, threshold=0.6, ...)
model2 = Scrabble(batch_size=10, ..)
f1 = F1(average=‘macro’)
workflow = Workflow(dataset=dataset, model=[model1,model2], metric=f1, out_format=‘brick’)
De-noising
Smoothing
Output Brickifier
Evaluator
Visualizer
Names/TS Data
Scrabble
Building Adapter
TS Data
Data Feature Extractor
Random Forest
De-noising
Smoothing
Point Names
Prog. Synthesis
Building Adapter
Zodiac
Evaluator
Notes: Enables: workflow\\benchmark\\Feature selection

## Slide 42: Thoughts…
Data “Context” will be increasingly important
In the context of
  Heterogeneous sources
  Repurposed data
  Missing metadata
  ...

## Slide 43: Future Work
overheated room
Notes: prioritize attention in data, building search engine\\
create context for all personal digital traces\\
secure and protect user's data since we can infer so much info

## Slide 44
Comfort
Correctness
Maintenance
Type Inference
Relation Inference
Context
Metadata
Mapping
Schema
Toolkit
Plaster
Questions?
Notes: ack before finish