## Slide 1
Towards Automatic Context Inference
for Sensors in Commercial Buildings

## Slide 2
Notes: People spend 93% of time indoors and providing a comfortable env can improve 8-11% productivity.
To ensure\\ that these buildings operate normally and are comfortable throughout diff weather conditions,
we need to assess and control various factors\\, such as air circulation, heat flow, moist. lv, or lgt cond.
To this end, 1000s of sensors are installed to monitor the speed of every fan, status of every water pipe, and the kw consumption of every circuit,\\

## Slide 3
Comfort
Correctness
Maintenance
Zone Temp 2 RMI204
Temp Floor 1 Area1
SODA1R300__ART
SODA1R410B_ART
Notes: On top of these sensors, nuanced intelligent analytics are running continuously\\
to optimize the comfort\\ assure the correctness\\ identify faulty and dysfunctional equip.
As an example, an analytics that detects overheated rooms would need to locate and pull data from the tmp & tmp stpt in each room\\
Such contextual information about the type and location of sensors is extracted from their point names, e.g., in bldg1\\ another two look completely diff\\
Diff buildings use diff naming vocabularies and conventions

## Slide 4
Zone Temp 2 RMI204
Temp Floor 1 Area1
SODA1R300__ART
SODA1R410B_ART
Comfort
Correctness
Maintenance
Comfort
Correctness
Maintenance
Metadata Mapping
Notes: Consequently, as a first step in running analytics\\, we need to create a match btw the data streams and the inputs of AE\\
This process is called metadata mapping and is currently a manual process performed on a per building basis

## Slide 5
SODA1R300__ART
Bldg: xxx
Zone: xxx
Room: xxx
Type: xxx
SOD
1
300
Room Temperature
EIA's 2012 Commercial Buildings Energy Consumption Survey
Notes: As an example, here you see\\ a technician with domain knowledge needs to manually segment the piont nemsand decode the information\\
It takes weeks for a typical bldg with thousands of sensors&points\\not scalable
Mapping one bldg could be 1M business\\ >savings, eat into benefits

## Slide 6
Comfort
Correctness
Maintenance
Type Inference
Relation Inference
Context
Metadata
Mapping
Schema
Toolkit
Plaster
Notes: My dissertation work tries to tackle this metadata mapping problem by proposing new methods that automatically extract type and relations\\
and providing a tool to express this information in a uniform format

## Slide 7
Comfort
Correctness
Maintenance
Type Inference
Relation Inference
Context
Metadata
Mapping
Schema
Toolkit
Plaster
Notes: To summarize, contributions b4 and after proposal.

## Slide 8: Sensor context can be inferred using names and data with minimal or no manual effort
Hypothesis
Notes: PAUSE

## Slide 9
Comfort
Correctness
Maintenance
Type Inference
Relation Inference
Context
Metadata
Mapping
Schema
Toolkit
Plaster

## Slide 10
SODA1R300_ART
SODA2R214_ART
SODA-ZONE2ART
SODA-AHU9-SFS
SODA3AHU7-SFS
1
Zone1 Temp RMI328
Space RMI530 TMP
DA Humiditydac4UIP17
Notes: given names and data, the goal is to automatically predict the types\\
we usually have well mapped bldgs; the challenge however, is how to transfer the info\\
On the one hand, pt name is a good indicator of the type, but the pattern does not generalize across buildings\\;
On the other hand, TS data is more likely to be similar between buildings, e.g., temp is 60-70 no matter which building\\
so we transfer the info in data by training a clf using data features\\ and apply the clf in the new bldg to predict types

## Slide 11
SODA1R300_ART
SODA2R214_ART
SODA-ZONE2ART
SODA-AHU9-SFS
SODA3AHU7-SFS
2
1
Notes: we can train a different clf to learn a different perspective of the data feautres

## Slide 12
SODA1R300_ART
SODA2R214_ART
SODA-ZONE2ART
SODA-AHU9-SFS
SODA3AHU7-SFS
3
1
2
Notes: and similarly a third

## Slide 13
SODA1R300_ART
SODA2R214_ART
SODA-ZONE2ART
SODA-AHU9-SFS
SODA3AHU7-SFS
1
2
3
0.67
0.33
0.67
Notes: however, each clf can give a different prediction, how to effectively adopt the preds?
people tend to name the same type of sensors similarly\\, so we look at how much the clf's preds agree with the name clusters, in order to quantify a clf's confidence
e.g., we cluster names and get 2 groups, we see that out of the 3 sensors\\, 2 are predicted as temps -- thus 2/3 = 0.67\\ we do so for each clf and take a weighted sum
Also set a threshold to assure confident preds

## Slide 14: Evaluation Dataset
A: Rice Hall
B: Soda Hall
C: Sutardja Dai Hall
3 buildings on 2 campuses
2,500+ sensing and control points
22 types

## Slide 15: Type Classification Accuracy by Transfer Learning
Cov: % labeled
Acc: % of labels are correct
Notes: x-axis: threshold
metrics, two-way transfer
trend: as acc goes up, cov goes down
mention the numbers:96acc/72cov 85acc/92cov

## Slide 16: Related Work
-Still require manual effort
-Work within a building
Schumann et al. - BuildSys’14
Bhattacharya et al. - BuildSys’15
Balaji et al. - BuildSys’15
Gao et al. - BuildSys’15
Koh et al. - BuildSys’18

## Slide 17: Follow-up work on Type Inference
lux
lux
Transfer Learning
Active Learning
?
?
?
?
?
?
Fully Automated Transfer Learning (this work)
Semi-Automated Active Learning
Notes: BA can automatically predict the type for a fraction of points,\\ some still remain unlabeled.
We still need human input\\ and resort to AL to reduce the #human input

## Slide 18: Clustering-based Active Learning
Humidity
?
?
?
?
?
?
?
Zone2 TMP RMI204
Zone2 TMP RMI228
Zone3 TMP RMI120
Zone4 HUM RMI 2014
Zone4 TMP RMI530
RMC104 HUMID
RMI328 HUM
Temperature
Temperature
Humidity
Humidity
Humidity
Temperature
Notes: As human input is costly, we want to predict the type using the minimal #human effort\\
Challenge: how to select the best examples for a human to label and train a clf?
Intuition: names of same type of sensors tend to be similar\\, so only need to select a few representatives
We cluster on pt names\\ and look at regions with max disagreement\\ pick representative from cluster center\\repeat

## Slide 19: Active Learning for Type Classification
Rice Hall
Classification Accuracy
More than
50% fewer
Notes: we evaluate and examine # of labels vs acc
if we look at 80% acc, we see > 50% reduction in the #human input

## Slide 20
Comfort
Correctness
Maintenance
Type Inference
Relation Inference
Context
Metadata
Mapping
Schema
Toolkit
Plaster

## Slide 21: Relation Inference
lux
AHU
VAV
AHU: Air Handling Unit
VAV: Variable Air Volume
Notes: Knowing the type alone is not enough, we also need to know the relations between points\\
e.g., functional connection btw ahu-vav for tracking down mechanical issues in equip\\,
or co-located sensors to assess if a room is comfortable or not.\\
Challenge: search space is huge considering all possible pairwise relations
Key: as they are connected, we would observe correlated events

## Slide 22
AHU
VAV
Notes: As an example, AHU-VAV, when the air flow changes in an AHU, we also observe correspondent changes in the connected VAV.
How do we detect the events?

## Slide 23
Outlier Detection?
Notes: OD will get the big one, another looks like no-event
if we tune the parameter to get 2nd, we will obtain many FPs.

## Slide 24
Kinematics?
Steady
Gradual
Drastic
Notes: We consider the kinematic states of data: steady vs dynamic
We hence model the state in data and consider the changes in state as events
The basic idea is to estimate the state of each reading\\ and the state determines how the data progresses over time, in terms of velocity and noise lv.\\ e.g., the red is steady\\blue gradual\\green drastic

## Slide 25: Switching Kinematic Model
latent true values
observed values
e.g., airflow sensor readings
xt-1
xt
xt+1
yt-1
yt
yt+1
zt-1
zt
zt+1
latent states
e.g., event or steady
Markovian state sequence
True value mapping
Kinematics transitions
Notes: More formally, the model is the following: \\top layer decides the state\\ and affects how data progress (vel, nosie) which is expressed by the 2nd layer
what’s new here: globally learn the para\\consider both backwards and forwards info

## Slide 26: Example Output
VAV
AHU 1
AHU 2
Notes: Example output of the event model: a vav and its connected AHU, and a non-connecting AHU.\\
We see the top correlates better with the 2nd than the 3rd; the intuition however is to use only events caused due to the connection\\
Besides these correlated events, VAVs are also affected by the activities in served space.

## Slide 27: Sift Out Coincident Events
Correlation Before After
<top, mid>: 0.73 0.87
<top, bottom>: 0.59 0.31
AHU
VAV 1
VAV 2
Notes: Masking to the rescue: when correlating a vav to an ahu, we only use events in the vav at T where ahu has events\\ e.g., (the pink ones)
Masking increases the corr between connected equip

## Slide 28: Evaluation Dataset
 | A | B | C | D | E
# of VAV | 261 | 113 | 195 | 510 | 259
# of AHU | 12 | 8 | 5 | 13 | 8
# of Sensor | 2,754 | 1,318 | 2,010 | 4,811 | 2,379

## Slide 29: Functional Relation Accuracy
Chart: 
| Random | Correlation | Canny Edge | Kalman Filter | Switching Kinematic Model
Method | 10.8 | 58.41 | 69.91 | 80.59 | 92.38
Inference Accuracy (%)
Notes: Explain baselines

## Slide 30: Effect of Amount of Data
Notes: As we look for more correlated events over a longer time, the chance of correlation by chance drops.

## Slide 31
lux
AHU
VAV
Notes: The principle of looking for correlated events also applies to co-location

## Slide 32
RM 1
RM 3
RM 2
Objective:
Higher sum of all red edges
lux
lux
lux
3.5
4.2
3.1
4.8
2.8
…
Notes: We want to assign sensors into rooms, and assume one for each type.\\ color of the sensor indicates its ground truth room membership.
optimize for a higher sum of the red edges, where each red edge is the pairwise corr of event sequences\\
Genetic algorithm: generate candidates by swapping pairs of same type\\, e.g., \\ \\
and replace the candidates low on the rank with the top ones – as in natural selection – the best survive

## Slide 33
RM 1
RM 3
RM 2
Objective:
Higher sum of all red edges
lux
lux
lux
4.2
4.8
…
4.2
4.8
3.5

## Slide 34: Evaluation Dataset
204 streams from 51 rooms in one office building
4 types: CO2, humidity, light, temperature
One week’s data

## Slide 35: Co-location Accuracy
Event
Raw
EMD
Notes: explain baselines and axis
looking for correlated events is effective in identifying co-located sensors

## Slide 36: Related Work
Smith et al. - SigBED’12
Koc et al. - BuildSys’14
Bharttacharya et al. - BuildSys’15
Koh et al. - Arxiv’16
-Different Relations
-Require Perturbations

## Slide 37
Comfort
Correctness
Maintenance
Type Inference
Relation Inference
Context
Metadata
Mapping
Schema
Toolkit
Plaster

## Slide 38
Power Meter
Supply Fan
VAV
Damper
Return Fan
AHU
VAV
AHU
Damper
feeds
Power Meter
hasPoint
hasPart
HVAC Zone
feeds
Integrated into the ASHRAE Standard 223P for semantic tagging of building data
Notes: After extracting the contextual information, we need to express it in a uniform format, i.e., a schema
Brick has an expressive and comprehensive vocabulary to represent the entities and their relationships\\ triplet predicate: e.g. \\ \\
it enables efficient and convenient queries.

## Slide 39
Comfort
Correctness
Maintenance
Type Inference
Relation Inference
Context
Metadata
Mapping
Schema
Toolkit
Plaster
Notes: We need a tool to automatically infer context and express the info following the schema

## Slide 40: Plaster Architecture
De-noising
Data Feature Extractor
Smoothing
Scrabble1
Zodiac2
Building Adapter
Prog. Synthesis3
Output Brickifier
Evaluator
Visualizer
Data Preparation
Algorithm
Utility
Feature Engineering
Model Training
Delivery
Input Brickifier
Text Feature Extractor
Canonical ML
1[KBSMAG BuildSys’17] 2[BVNA BuildSys’15] 3[BHCOWW BuildSys’15]
Notes: Plaster consists of reusable modules, and provides unified interfaces to construct algorithms.

## Slide 41: Workflows
from plaster.utils import DataLoader
from plaster.utils import Dataset
from plaster.utils.preprocessing import denoise, smooth
from plaster.algorithms import BuildingAdapter
from plaster.algorithms import Scrabble
from plaster.workflow import Workflow
raw_data = DataLoader(building=‘rice’)
dataset = Dataset(raw_data, type=‘time_series’, preprocessing=[denoise,smooth])
model1 = BuildingAdapter(batch_size=1, threshold=0.6, ...)
model2 = Scrabble(batch_size=10, ..)
f1 = F1(average=‘macro’)
workflow = Workflow(dataset=dataset, model=[model1,model2], metric=f1, out_format=‘brick’)
De-noising
Smoothing
Output Brickifier
Evaluator
Visualizer
Input Brickifier
Scrabble
Building Adapter
Input Brickifier
Data Feature Extractor
Random Forest
De-noising
Smoothing
Input Brickifier
Scrabble
Building Adapter
Zodiac
Evaluator
Notes: Enables: workflow\\benchmark\\Feature selection

## Slide 42: Thoughts…
Data “Context” will be increasingly important
In the context of
  Heterogeneous sources
  Repurposed data
  Missing metadata
  ...

## Slide 43: Thesis Contributions
Automatic type inference
  Complemented by a semi-automated method
Automatic relation inference
  Functional connections between equipment
  Co-location
Toolkit for mapping to Brick schema

## Slide 44: What’s Next…
overheated room
Notes: prioritize attention in data, building search engine\\
create context for all personal digital traces\\
secure and protect user's data since we can infer so much info

## Slide 45
Rajesh Gupta
Jason Koh
David Culler
Arka Bhattacharya
Gabriel Fierro
Mani Srivastava
Bharathan Balaji
Joern Ploennigs
Jorge Ortiz
Jingkun Gao
Yuvraj Agarwal
Mario Berges
Joshua Gluck
Mikkel Kjaergaard
Aslak Johansen
Kamin Whitehouse
Hongning Wang
Quanquan Gu
Avinash
Kalyanaraman
Elahe
Soltanaghaei
Erin
Griffiths

## Slide 46
Comfort
Correctness
Maintenance
Type Inference
Relation Inference
Context
Metadata
Mapping
Schema
Toolkit
Plaster
Questions?
Notes: ack before finish

## Slide 47: Backup Slides

## Slide 48: Type Inference
What kind of sensor is this?
Notes: next, lets
transition from type to function
future steps

## Slide 49: Functional Relationships
How are these sensors related?

## Slide 50
Comfort
Correctness
Maintenance
Schema
Type Inference
Relation Inference
Context
Metadata
Mapping
Toolkit
Plaster

## Slide 51
SODA1R300_ART
SODA-SW53_LGT
SODA-ZONE2MTN
SOD-AHU1-SFS
SODA1VAV4-CO2
Name
Timeseries
Type
Functional
Relation
Co-location
Notes: some primers: we exploit two common attributes of each sensor
We focus on *two kinds* of metadata
First is type\\, another is relationship\\ eg: \\ \\

## Slide 52
Notes: show two vavs

## Slide 53
Edge Detection?

## Slide 54: Transfer Learning Implementation
Name Clustering
K-mers features, for k=3,4
DPGMM clustering
Time Series Classification
Features
  min
  max
  median
  variance
  …
SVM, Logistic Regression, and Random Forest
Zone-Temp2__RMI204
{zon, one, tem, emp, rmi, zone, temp}

## Slide 55
Accuracy (Percentage)
Coverage (Labeled Percentage)
Accuracy vs Coverage
Notes: setup the axis
talk about one, threshold on agreement to admit a label, the trend\\
then show\\ others and the specific pts
for an application, we probably need acc high enough, say 85,\\ but we see most of the cases end up with <85% points being labeled, so how to address the unlabeled sensors?

## Slide 56: Combining Multiple Buildings as the Source
More Sources, More Promising!

## Slide 57
Building A
Classification Accuracy
Effect of Clustering on Accuracy
Original
Notes: Adding clustering alone is no better than LM
After adding p it gets better because xxx
LM+P is bad on A because loose estimation of r
Expalin setup and better legend would be easier

## Slide 58
Building A
Classification Accuracy
Effect of Label Propagation on Accuracy
Original
Notes: Adding clustering alone is no better than LM
After adding p it gets better because xxx
LM+P is bad on A because loose estimation of r
Expalin setup and better legend would be easier

## Slide 59: Cross-Predictive Clustering
1
2
3
4
Time t
Time t-1
= w12*
+ w13*
+ w14*
Time t-1
Time t-2
= w12*
+ w13*
+ w14*
w11 w12 w13 w14
…...
T
d
T < d
T
Notes: what leads to high-d\\ challenge?
a new metric

## Slide 60: Cross-Predictive Clustering
The estimator:
Notes: better explaination

## Slide 61: Evaluation
204 streams from 51 rooms in one office building
4 different types
One week’s data
Notes: how the baseline works
add clustering number on pts
this is better, should give better acc for the first 2
and see if it can work for things other than type.

## Slide 62: Clustering Results
, d=204, T=336
Notes: T and d for real data
highlight my approach
title

## Slide 63: Cross-Predictive Clustering Models
(d time series of length T )
The input:
The vector autoregressive model:

## Slide 64: Cross-Predictive Clustering
The estimator:
Notes: better explaination

## Slide 65: Switching Kinematic Model
latent true values
observed values
e.g., airflow sensor readings
xt-1
xt
xt+1
yt-1
yt
yt+1
zt-1
zt
zt+1
latent states
Notes: use k=2 as ex
what’s new here

## Slide 66: In the Thesis Other Work
IPSN’12
SenSys’12a
SenSys’12b
IPSN’13
MobiSys’13
UbiComp’17
Type
Relation
Context
Schema
BuildSys’15a, BuildSys’15b
CIKM’15, AISTATS’17
BuildSys’13, UnderReview’19
BuildSys’16
BuildSys’18
Toolkit
Plaster
Notes: sw by far, also hw
released for framework

## Slide 67
AHU
VAV
VAV
Notes: why relation: we have type but not knowing which are in the same room
what they are sensing and why correlated
intuition: air from a to v, thus exhibit correlated events
challenge: how to detect and locate correlated events\\

## Slide 68
?
?
?
?
?
SODA1R300_ART
?
SODA-SW53_LGT
SODA-ZONE2MTN
SODA-AHU9-SFS
SODA4VAV74-CO2
Name
Data
Type
Co-location
Functional
Relation
93%
8~11%